Sika Sarnafil®

Green Roof –

Intensive

Grid System PMA

Waterproofing

Specification

Protected Membrane Assembly (PMA)

DISCLAIMER

All information provided by Sika Corporation (“Sika”) concerning Sika products, including but not limited to, any recommendations and advice relating to the application and use of Sika products, is given in good faith based on Sika’s current experience and knowledge of its products when properly stored, handled and applied under normal conditions in accordance with Sika’s instructions. In practice, the differences in materials, substrates, storage and handling conditions, actual site conditions and other factors outside of Sika’s control are such that Sika assumes no liability for the provision of such information, advice, recommendations or instructions related to its products, nor shall any legal relationship be created by or arise from the provision of such information, advice, recommendations or instructions related to its products. The user of the Sika product(s) must test the product(s) for suitability for the intended application and purpose before proceeding with the full application of the product(s). Sika reserves the right to change the properties of its products without notice. All sales of Sika product(s) are subject to its current terms and conditions of sale which are available at usa.sarnafil.sika.com or by calling 800-451-2504.

Prior to each use of any Sika product, the user must always read and follow the warnings and instructions on the product’s most current Product Data Sheet, product label and Safety Data Sheet which are available online at usa.sarnafil.sika.com or by calling Sika's Technical Service Department at 800-451-2504. Nothing contained in any Sika materials relieves the user of the obligation to read and follow the warnings and instruction for each Sika product as set forth in the current Product Data Sheet, product label and Safety Data Sheet prior to product use.

Sika warrants this product for one year from date of installation to be free from manufacturing defects and to meet the technical properties on the current Product Data Sheet if used as directed within shelf life. User determines suitability of product for intended use and assumes all risks. Buyer’s sole remedy shall be limited to the purchase price or replacement of product exclusive of labor or cost of labor.

NO OTHER WARRANTIES EXPRESS OR IMPLIED SHALL APPLY INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE. SIKA SHALL NOT BE LIABLE UNDER ANY LEGAL THEORY FOR SPECIAL OR CONSEQUENTIAL DAMAGES. SIKA SHALL NOT BE RESPONSIBLE FOR THE USE OF THIS PRODUCT IN A MANNER TO INFRINGE ON ANY PATENT OR ANY OTHER INTELLECTUAL PROPERTY RIGHTS HELD BY OTHERS.

Introduction

Loose-Laid Sheet With Containment Grids Waterproofing System For Intensive Green Roofs	2

System Description	2

System Components	2

Regional Offices	3

Part 1 – General Conditions

1.01 Description	1

1.02 Quality Assurance	1

1.03 Submittals	2

1.04 Product Delivery, Storage and Handling	2

1.05 Job Conditions	3

1.06 Sequencing of the Work	4

1.07 Bidding Requirements	4

1.08 Warranties	4

Part 2 - Products

2.01 Waterproofing Membrane	4

2.01 System Flashing Products and Accessories	5

2.01 Vector Mapping Grid and Connections	7

2.02 Leveling and Separation Layers	7

2.01 Drainage Composite	7

2.02 Insulation	8

2.03 Precast Concrete Pavers and Pedestals	8

2.01 Related Materials	8

Part 3 – Execution

3.01 Examination	9

3.02 Substrate Preparation	9

3.03 Containment Grid Installation	10

3.04 Control Test Drain Installation	11

3.05 Vector Mapping Grid and Connections Installation	11

3.06 Leveling and Separation Layer Installation	11

3.01 Thermoplastic Waterproofing Membrane Installation	11

3.02 Hot-Air Welding of Lap Areas	12

3.03 Membrane Flashings	12

3.04 Sarnaclad Metal Flashings	13

3.05 Temporary Cut-Off	13

3.06 Water Testing of Drains and Electronic Leak Detection Testing 	13

3.01 Installation of Drainage Composites	14

3.02 Insulation and Filter Fabric Installation	14

3.03 Precast Concrete Paver System	14

3.04 Monitoring the Vegetative Cover Installation	14

3.05 Details	15

INTRODUCTION TO

SIKA SARNAFIL® LOOSE-LAID SHEET WITH CONTAINMENT GRIDS

WATERPROOFING SYSTEM

FOR INTENSIVE GREEN ROOFS

System Description

The Sika Sarnafil Loose-Laid Sheet with Containment Grids Waterproofing System (Grid System) is designed to protect structures from the effects of water infiltration leading to structural deterioration and interior water damage.  The system is primarily intended for intensive green roof applications with more than 6 inches (152 mm) of growth media and plantings as overburden, but is also applicable for plaza decks, parking decks, tunnels, planters, balconies/terraces, and roofing applications utilizing pavers or concrete as overburden.

The Grid System design combines the performance characteristics of an adhered system with the ease of installation of a loose-laid system.  The Grid System design consists of thermoplastic membrane strips which are fully adhered to the substrate to form a grid pattern.  The Sarnafil G476 waterproofing membrane is loose-laid on a leveling layer over the substrate and hot-air welded to the containment grid strips.

The Grid System provides the means to effectively determine the location of water entry, restrict the migration of moisture from one grid area to another, and most importantly minimize the amount of overburden to be removed if leakage were to occur after installation.

System Components

The Grid System design includes the following:

| #### Sikaflex-11FC. #### Sarnafil G459 Grid Strip Membrane. #### Sarnafelt NWP-HD Leveling Layer. #### Sarnafil G476 Waterproofing Membrane. | #### Sika Sarnafil Drainage Layer. #### Sarnatherm XPS Insulation (optional). #### Filter Fabric. |
| --- | --- |

REGIONAL OFFICES

| NEW ENGLAND REGION 225 Dan Road Canton, MA 02021 Phone:(781) 821-0865 Fax:(781) 821-9205 EASTERN REGION One Park Way 3rd Floor Upper Saddle River, NJ 07458 Phone:(201) 327-0479 Fax:(201) 327-4069 SOUTHERN REGION 3483 Satellite Boulevard Duluth, GA 30096 Phone:(770) 495-0025 Fax:(770) 495-0027 MIDWEST REGION 200 W. 22nd St., Suite 216 Lombard, IL 60148 Phone:(800) 532-5123 Fax:(630) 620-9646 | SOUTHWEST REGION 2517 Fairway Park, Suite 200 Houston, TX 77092 Phone: (713) 812-0102 Fax: (713) 812-0107 MOUNTAIN REGION 2881 South 900 West Salt Lake City, UT 84119 Phone:(801) 575-8648 Fax:(801) 355-4407 WESTERN REGION NORTH 2375 Rodolfo Court Sparks, NV 89436 Phone:(775) 626-7701 Fax:( 775) 626-7703 WESTERN REGION SOUTH 6590 Darin Way Cypress, CA 90630 Phone:(714) 898-9355 Fax:(714) 898-9357 |
| --- | --- |
| WEB ADDRESS: www.sikacorp.com | EMAIL ADDRESS: webmaster.sarnafil@us.sika.com |
| SIKA CANADA - ROOFING 6915 Davand Drive Mississauga, ON L5T 1L5 Phone:(905) 795-3177 Fax:(905) 795-3192 www.sika.ca |  |

SECTION 07 54 19

THERMOPLASTIC MEMBRANE WATERPROOFING

LOOSE-LAID CONTAINMENT GRID SYSTEM

[NOTE TO SPECIFIER:  NOTES TO SPECIFIER ARE DESIGNATED BY [ ].  SPECIFIER IS TO SELECT ONE OF THE OPTIONS PROVIDED FOR PROJECT SPECIFIC SPECIFICATIONS.]

TO DISPLAY OR HIDE SPECIFIER NOTES

MS Word (2007 and later):	MS Word (prior to 2007):

1. Select the OFFICE logo or FILE in the upper left corner.	1. Select TOOLS.

2. Select OPTIONS.	2. Select OPTIONS.

3. Select DISPLAY on the left menu.	3. Select VIEW.

4. Select HIDDEN TEXT under “Always Show These”.	4. Select HIDDEN TEXT.

This guide specification is intended for intensive green roof applications. Because of the heavy loads associated with these applications, the supporting deck is typically structural concrete.

# GENERAL CONDITIONS

## DESCRIPTION

### Scope

To install a loose laid thermoplastic membrane waterproofing system with containment grids with integral flashings and other components.

The work includes but is not necessarily limited to the following:

#### Substrate Preparation

#### Containment Grids

#### Control Test Drains (If Specified)

#### Vector Mapping Grid and Connections (If Required)

#### Geotextile Leveling Layer

#### Waterproofing Membrane

#### Membrane Flashings

#### Metal Flashings

#### Drainage Layer

#### Insulation (If Specified)

#### Sealants and Adhesives

#### Monitoring the Installation of Vegetative Cover

#### Pavers (If Specified)

### Related Work under Other Sections

[NOTE TO SPECIFIERS:  SPECIFY OTHER RELATED SECTIONS SUCH AS VEGETATIVE COVER, CONTRACT DOCUMENTS, SITE WORK, PLUMBING, ETC.]

˙

## QUALITY ASSURANCE

- This waterproofing system shall be applied only by a waterproofing Applicator authorized by Sika Sarnafil prior to bid. All work shall be completed by Sika Sarnafil trained personnel.

- Installation of containment grids, leveling layer, waterproofing membrane, separation layer, flashing membrane, expansion joints, membrane protection layer, drainage layer and insulation shall be the responsibility of the waterproofing applicator to ensure undivided responsibility.

- Obtain primary waterproofing materials, membrane and flashings, from a single manufacturer with not less than 20 years of successful experience in waterproofing application.  Provide other system components only as approved by manufacturer of primary materials.

- Pre-construction conference to be held with the owner, architect, Applicator’s field superintendent, waterproofing foreman, Sika Sarnafil representative, and other involved trades to discuss waterproofing practices applicable to this project.

- There shall be no deviation made from the contract specification or the approved shop drawings without prior written approval by the owner or the owner’s representative, and/or design professional, and Sika Sarnafil.

- The Applicator shall follow Sika Sarnafil’s most current quality assurance procedures.

- Cross-section seam samples shall be taken by the applicator a minimum of two times a day (AM/PM) through completed seams and evaluated immediately.  The samples must be dated and saved for evaluation by a Sika Sarnafil Technical Representative. Each test cut shall be patched by the Applicator.

- Test grid strips approximately 2 – 3 feet long shall be installed by the applicator to test the adhesion prior to the actual installation in representative areas.

- Membrane Testing for Water Tightness

      - Water Testing of Drains

The Applicator shall water test drains according to Sika Sarnafil’s most current Quality Assurance Procedures. See Section 3.12.

### [NOTE TO SPECIFIERS: ELECTRONIC LEAK DETECTION TESTING IS REQUIRED WHEN A SYSTEM WARRANTY IS SPECIFIED, AND IT IS THE ONLY ACCEPTABLE QUALITY ASSURANCE METHODOLOGY. ELECTRONIC LEAK DETECTION TESTING IS RECOMMENDED, BUT NOT REQUIRED, FOR A MEMBRANE WARRANTY. SEE TECHNICAL BULLETIN #15-7 FOR IMPORTANT INFORMATION CONCERNING THE USE OF ELECTRONIC LEAK DETECTION FOR LOCATING LEAKS THROUGH OVERBURDEN.]

˙

#### Electronic Leak Detection Testing

Electronic Leak Detection Testing (System Warranty) – The waterproofing applicator shall arrange for testing through Sika Sarnafil.  See Section 3.06.

Electronic Leak Detection Testing (Membrane Warranty) – The waterproofing applicator shall arrange for testing by a qualified testing agency.  See Section 3.06.

## SUBMITTALS

### The Applicator shall submit to the owner’s representative and/or design professional the following:

#### A letter from Sika Sarnafil certifying that the Applicator is an approved waterproofing applicator in good standing.

#### Specimen copy of Sika Sarnafil’s warranty.

#### Specimen copy of Applicator’s warranty.

## PRODUCT DELIVERY, STORAGE AND HANDLING

### All products delivered to the job site shall be in the original unopened containers or wrappings.

### Handle all materials to prevent damage.  All materials shall be placed on pallets and fully protected from moisture with canvas tarpaulins.

### Membrane rolls shall be stored lying down on pallets and fully protected from moisture with canvas tarpaulins.

### Bonding adhesives shall be stored at temperatures above 40 degree F (5 degree C).

### All flammable materials shall be stored in a cool dry area away from sparks and open flames.  Follow precautions outlined on container or supplied by the material manufacturer/supplier.

### Any materials which the owner’s representative and/or Sika Sarnafil determine to be damaged are to be removed from the job site and replaced at no cost to the owner.

## JOB CONDITIONS

- Proceed with waterproofing membrane installation only after substrate preparation is complete.  Owner’s representative and/or design professional and waterproofing Applicator must accept substrate before proceeding with membrane installation.

- Substrate must be clean and smooth.  With the exception of areas to receive grid strips, damp concrete is acceptable, however no standing or visible water is allowed.  Do not work in rain or snow or adverse weather conditions.  Severe temperatures, moisture and humidity may affect the installation of products during construction.  Comply with applicable installation requirements for all components.

- All work shall be scheduled and executed without exposing the completed waterproofing system and interior building areas to the affects of inclement weather.  The building and its contents shall be protected against all risks.

- The structure must be designed to support the system, including the vegetative cover.  The adequacy of the structural support must be verified in writing by the owner, the owner’s design professional, architect, or engineer. The Applicator shall take precautions that storage and/or application of materials and/or equipment does not overload the deck or building structure.

- All new and temporary construction, including equipment and accessories, shall be secured in such a manner, at all times, as to preclude wind blow-off or damage.

### Liquid materials such as solvents and adhesives shall be stored and used away from open flames, sparks and excessive heat.

### The Applicator should take necessary precautions when using adhesives or surface conditioner around air in-takes.  The smell of the adhesive, primer, or surface conditioner could be a disturbance to the building owner and occupants.  It is the Applicator’s responsibility to notify the owner and take the proper precautions.

### The Applicator shall verify that all drain lines are connected and un-blocked before starting work.  Report any blockages or non-connected drains to the owner’s representative and/or design professional in writing.

### The Applicator is cautioned that Sarnafil membranes are incompatible with asphalt, coal-tar, polystyrene, oil-based and plastic-based cements, creosote, penta-based materials, grease, fats, oils, and solvents. Such materials shall not come in contact with the waterproofing membrane at any time.  If such contact occurs, the material shall be cut-out, discarded and patched.

### Arrange work sequence to avoid use of newly installed waterproofing for storage, walking surface, and equipment movement.  Where such access is absolutely required, the Applicator shall provide all necessary temporary protection and barriers to segregate the work area and to prevent damage to adjacent areas.  Adequate protection of the membrane shall be provided for all waterproofing areas which receive traffic during construction.  Any damage which occurs to the waterproofing membrane and/or system is to be brought to the attention of the owner’s representative and/or design professional and Sika Sarnafil.  All damage is to be repaired according to Sika Sarnafil’s recommendations.  The party responsible for damage shall bear the cost of repairs.

### All waterproofing materials, insulation, flashings and metal work removed for construction shall be immediately taken off the site to a legal dumping area authorized to receive such materials.

### If any unusual or concealed condition is discovered, stop work and notify the owner’s representative and/or design professional and Sika Sarnafil immediately, in writing.

### Site cleanup, including both interior and exterior building areas in any way affected by the construction, shall be complete and to the owner’s satisfaction.  All landscaped areas affected by waterproofing activities shall be raked clean and seeded, if required.  All paved areas shall be swept clean. All areas stained, dirtied, and discolored or otherwise damaged due to waterproofing activities shall be cleaned, restored, and replaced as required.

## SEQUENCING OF THE WORK

### Do not proceed with installation of subsequent layers and vegetative cover over the completed sections of the waterproofing without the acceptance of the owner’s representative, design professional, general contractor, and Sika Sarnafil (when a System warranty is specified). A copy of the Final Inspection for Warranty is considered acceptance from Sika Sarnafil.

### Protect the membrane and coordinate with other trades to avoid traffic over completed membrane surfaces.

## BIDDING REQUIREMENTS

[NOTE TO SPECIFIERS:   DELETE THIS SECTION FOR NEW CONSTRUCTION PROJECTS.]

˙

### Pre-Bid Meeting

A pre-bid meeting shall be held with the Owner's Representative and involved trades to discuss all aspects of the project.  The Applicator's field representative or roofing foreman for the work shall be in attendance.  Procedures to avoid rooftop damage by other trades shall be determined.

### Site Visit

Bidders shall visit the site and carefully examine the areas in question as to conditions that may affect proper execution of the work.  All dimensions and quantities shall be determined or verified by the contractor.  No claims for extra costs will be allowed because of lack of full knowledge of the existing conditions unless agreed to in advance with the Owner or Owner's Representative.

## WARRANTIES

### General

#### A Sika Sarnafil Representative’s presence on a project regardless of reason, length, or frequency, does not imply that any additional coverage beyond that stated in the warranty is in effect.

### Applicator’s Warranty

The Applicator shall supply the owner with a minimum two-year workmanship warranty. The warranty obligation shall run directly to the owner with a copy to Sika Sarnafil.

### Sika Sarnafil Warranty

[NOTE TO SPECIFIERS:  SELECT THE WARRANTY TYPE AND LENGTH BELOW.]

˙

#### Membrane Warranty (5, 10, 15, or 20 Years)

The Applicator shall provide a Sika Sarnafil membrane warranty to the building owner at the successful completion of the project.  The warranty shall cover defective waterproofing membrane.

#### System Warranty (5, 10, 15, or 20 Years)

˙

The Applicator shall provide a Sika Sarnafil System warranty to the building owner. Upon successful completion of the work to Sika Sarnafil's satisfaction and receipt of final payment, the Sika Sarnafil System Warranty shall be issued.

# PRODUCTS

General

Consult Product Data Sheet for additional information on Sika Sarnafil products.

##### WATERPROOFING MEMBRANE

### The manufacturer of the thermoplastic waterproofing membrane system shall have a track record of producing and marketing a reinforced PVC sheet system for waterproofing applications for at least 20 years and guarantee that the membrane thickness meets or exceeds [the specified thickness] when tested according to ASTM D751.  Subject to this and other technical requirements, provide products of the following:

1.	Sika Sarnafil, A Division of Sika Corporation, Canton, Massachusetts

Thermoplastic membrane: polyvinyl chloride (PVC) flexible sheets with non-woven fiberglass reinforcing.

#### [NOTE TO SPECIFIERS:  80 MILS IS THE STANDARD THICKNESS FOR SARNAFIL WATERPROOFING MEMBRANE AND IT IS RECOMMENDED FOR MOST APPLICATIONS. DURABILITY AND PUNCTURE RESISTANCE IS A FUNCTION OF MEMBRANE THICKNESS. DO NOT USE G476 IN SITUATIONS WHERE THE MEMBRANE WILL BE PERMANENTLY EXPOSED TO SUNLIGHT.]

˙

                - Sarnafil G476-15, 60 mil (1.5 mm), thermoplastic flashing membrane with fiberglass reinforcement.

Sarnafil G476-20, 80 mil (2.0 mm), thermoplastic flashing membrane with fiberglass reinforcement.

Parameters	ASTM Test Method	Typical Physical Properties

Membrane thickness, inches (mm)	D 638	0.060 (1.5)

Tensile Strength, psi.	D 751	1631

Elongation at Break, %	D 751	279 MD, 267 CMD

Seam Strength, % of Tensile Strength	D 751	86%

Retention of Properties After Heat Aging	D 3045

Tensile Strength, % of original	D 751	90%

Elongation at Break, % of original	D 751	90%

Tear Resistance, lbf	D 1004	21.0

Linear Dimensional Change, %	D 1204	0.0

Weight Change after immersion in water, %	D570	1.5

Static Puncture Resistance, 33 lbs. 	D5602	Pass

Dynamic Puncture Resistance, 10 J	D5635	Pass

##### SYSTEM FLASHING PRODUCTS AND ACCESSORIES

### Flashing

[NOTE TO SPECIFIERS:  BELOW YOU WILL FIND THE VARIOUS SARNAFIL FLASHING MEMBRANES USED FOR FLASHINGS AND PENETRATIONS.  THE FLASHING MEMBRANE SHOULD BE SPECIFIED AT THE SAME THICKNESS AS THE WATERPROOFING MEMBRANE.  IF DIFFICULT DETAILS EXIST (I.E. PIPES) A LESSER THICKNESS MEMBRANE MAY BE SPECIFIED.  SELECT APPROPRIATE PRODUCT BELOW.]

˙

#### Non-exposed flashings

                - Sarnafil G476-15, 60 mil (1.5 mm), thermoplastic flashing membrane with fiberglass reinforcement.

                - Sarnafil G476-20, 80 mil (2.0 mm), thermoplastic flashing membrane with fiberglass reinforcement.

#### Exposed flashings

                - Sarnafil G410-15, 60 mil (1.5 mm), thermoplastic flashing membrane with fiberglass reinforcement.

                - Sarnafil G410-20, 80 mil (2.0 mm), thermoplastic flashing membrane with fiberglass reinforcement.

#### Sarnafil G459-15, 60 mil (1.5 mm), thermoplastic, asphalt resistant, grid and flashing membrane with fiberglass reinforcement.

### Adhesives

#### Sarnacol 2170

Solvent-based adhesive for membrane flashings.

#### Sarnacol 2121

Water-based adhesive for membrane flashings.

#### Sikaflex-11FC

#### Membrane adhesive for containment grid strips and certain flashing details.

### Attachment Components

#### Sarnabar-SS

Heavy-duty, 14 gauge, roll-formed stainless steel bar used to attach membrane to decks.

#### Sarnastop

#### An extruded aluminum, flat low profile bar used to terminate flashing membrane.

#### Masonry Anchor

A drive-pin expansion type fastener with zinc sheaths and stainless steel pins for attachment of Sarnabar and Sarnastop to concrete, masonry, and brick.

### Accessories

#### Sikaflex Primer 449

A solvent-based primer used to prime the back of G459 grid strip membrane to improve adhesion to Sikaflex-11FC.

#### Sarnaclad-SS

A PVC-coated, heat weldable sheet metal capable of being formed into a variety of shapes and profiles.  Sarnaclad is a stainless steel sheet metal with an unsupported Sarnafil membrane laminated on one side for buried or concealed flashing conditions.

#### Sarnaclad

#### A PVC-coated, heat-weldable sheet metal capable of being formed into a variety of shapes and profiles.  Sarnaclad is a 25 gauge, G90 galvanized metal sheet with a 20 mil (1 mm) unsupported Sarnafil membrane laminated on one side for above grade flashing locations.

#### Aluminum Tape

A pressure-sensitive aluminum tape used as a separation layer between small areas of asphalt contamination and as a bond-breaker under the cover strip at Sarnaclad joints.

#### Sarnamatic

220 volt, self-propelled, hot-air welding machine used to seal long lengths of Sarnafil membrane seams.

#### Sarnacorner-Inside/Outside

Prefabricated inside and outside flashing corners made of PVC membrane that are heat-welded to membrane or Sarnaclad base flashings.

#### Sikaflex®-1a

Sealant used at flashing terminations and pitch pocket filler.

#### Multi-Purpose Tape

#### A high performance sealant tape used with metal flashings as a preventive measure against air and wind blown moisture entry.

#### Sarnacircle

Circular 48 mil (1.2 mm) G410 membrane patch welded over T-joints formed by overlapping membranes greater than 60 mil (1.5 mm) in thickness.

#### Sarnacord-PVC

A 5/32 inch (4 mm) diameter, red-colored, flexible thermoplastic extrusion that is welded to the top surface of the Sarnafil membrane against the outside edge of Sarnabar-SS, used to hold the membrane in position.

#### Sarnavap-10

A 10 mil (0.25 mm) thick polyethylene sheet used for a coal-tar pitch barrier.

#### Control Test Drain

A clear collection vessel installed through the structural deck in each grid area.  The vessel allows for periodic inspection for leakage.

##### VECTOR MAPPING GRID AND CONNECTIONS

[NOTE TO SPECIFIERS:  VECTOR MAPPING GRID IS REQUIRED WHEN AN EXISTING PRODUCT ON THE DECK WILL REMAIN (GO-OVER)].

### Vector Mapping Grid (VMG™)

### A specially selected 2” x 2” (50 mm x 50 mm) 304 stainless steel grid that serves as a conductive medium below the membrane used in conjunction with EFVM®.

### EFVM Connection Kit

### Connects the Vector Mapping Grid to the leak detection equipment. It consists of two (2) 0.45 mm, 6” x 6” SS 304 stainless steel EFVM connection plates, insulated, exterior graded 16 gauge low voltage wire, 5’-6” in length.  The EFVM Connection Kit is utilized to electrically energize the Vector Mapping Grid during the EFVM test.

##### LEVELING AND SEPARATION LAYERS

### Sarnafelt NWP-HD

A non-asphaltic, non-woven polypropylene felt leveling layer used between concrete and waterproofing membrane.

### Sarnafelt NWP

A non-asphaltic, non-woven 9 oz/yd2 (305 gms/m2) polypropylene felt separation layer used as an additional protective layer as required.

##### DRAINAGE COMPOSITE

[NOTE TO SPECIFIERS:  SELECT A DRAINAGE COMPOSITE FROM THE CHOICES BELOW.]

˙

### Drainage Composite 3811R

A 100% recycled polypropylene drainage core of fused, entangled filaments with a geotextile fabric bonded to each side.

### Geonet B

A polymeric drainage net with polypropylene geotextile laminated to both sides.  Recommended for heavy traffic areas requiring higher compressive strength but where lower flow rates are acceptable.

##### INSULATION

### Sarnatherm XPS

Extruded polystyrene closed-cell foam insulation. Thicknesses and compressive strength as noted on Project Drawings.

##### PRECAST CONCRETE PAVERS AND PEDESTALS

[NOTE TO SPECIFIERS:  SELECT ONE OF THE FOLLOWING.]

### Pavers shall be hydraulically pressed concrete units manufactured by Hanover Architectural Products or Oldcastle/Westile Inc., and supplied by Sika Sarnafil.

#### Precast Concrete Pavers and Pedestal System by Hanover Architectural Products and supplied by Sika Sarnafil.

#### Precast Concrete Pavers and Pedestal System by Oldcastle/Westile Inc. and supplied by Sika Sarnafil.

#### Concrete pavers shall comply with the following minimum requirements:

| Physical Property | ASTM Test Method | Requirements |
| --- | --- | --- |
| Dimensional Tolerances | C140 | As specified ±1/8 inch maximum |
| Compressive Strength | C140 | 8000 psi minimum |
| Flexural Strength | C293 | 725 psi minimum |
| Freeze Thaw Resistance | C67 | 25 cycles, max. 1% loss |
| Water Absorption | C140 | 5% or less |

[NOTE TO SPECIFIERS:  CONSULT HANOVER OR OLDCASTLE/WESTILE PRODUCT DATA SHEETS AND LITERATURE FOR AVAILABLE DIMENSIONS, COLORS, FINISHES, AND PEDESTAL SYSTEMS.]

˙

#### Precast Concrete Paver thickness shall be: ______

#### Precast Concrete Paver finish shall be: ______

#### Precast Concrete Paver color shall be: ______

#### Precast Concrete Paver size shall be: ______

#### Pedestal System shall be: ______

##### RELATED MATERIALS

### Wood Nailer

Wood nailers shall be treated for fire and rot resistance (ACQ treated) and be #2 quality or better lumber.  Creosote or asphalt-treated wood is not acceptable.  Wood nailers shall conform to Factory Mutual Loss Prevention Data Sheet 1-49.  All wood shall have a maximum moisture content of 19% by weight on a dry-weight basis.

[NOTE TO SPECIFIERS:  WOOD NAILERS OR WOOD BLOCKING FOR SOIL RETENTION SHALL BE INSTALLED PRIOR TO THE INSTALLATION OF THE MEMBRANE WHENEVER POSSIBLE.]

˙

### Plywood

When adhering the flashing membrane directly to plywood, a minimum 1/2 inch (13 mm) CDX (C side out), smooth-surfaced exterior grade plywood with exterior grade glue shall be used.  Rough-surfaced plywood or high fastener heads will require the use of Sarnafelt behind the flashing membrane.  Plywood shall have a maximum moisture content of 19% by weight on a dry weight basis.

### Miscellaneous Fasteners and Anchors

Fasteners are to be compatible with materials in contact with fasteners.  All fasteners and anchors shall have a minimum embedment of 1-1/4 inches (31.7 mm) and shall be approved for such use by the fastener manufacturer.  Fasteners for attachment of metal to wood blocking shall be annular ring nails.  Fasteners for attachment of metal to masonry shall be all-metal expansion type fasteners.  All fasteners shall meet Factory Mutual Standard 4470 for corrosion resistance.

# EXECUTION

###### EXAMINATION

- Examine all surfaces scheduled to receive waterproofing membrane and flashing for roughness, contaminants, unsound structural substrates or other conditions that may impair the waterproofing application.  Notify the owner and copy Sika Sarnafil in writing of any such conditions. Do not commence work until all defects are remedied.

- Applicator shall be responsible for acceptance or provision of proper substrate to receive new waterproofing materials.

- Applicator shall verify that the work done under related sections meets the following conditions:

#### Roof drains and/or scuppers have been reconditioned and/or replaced and installed properly.

#### Roof curbs, nailers, equipment supports, vents and other roof penetrations are properly secured and prepared to receive new roofing materials.

#### All surfaces to receive grid strips and flashings are smooth and free of dirt, debris and incompatible materials.

###### SUBSTRATE PREPARATION

[NOTE TO SPECIFIER:  THIS WATERPROOFING SYSTEM IS INTENDED TO BE USED OVER CAST IN PLACE CONCRETE. IT CAN NOT BE USED OVER WOOD, STEEL, OR LIGHTWEIGHT INSULATION FILL DECKS.]

[NOTE TO SPECIFIERS:  FROM THE CHOICES BELOW, SELECT THE APPROPRIATE SUBSTRATE PREPARATION DEPENDING ON WHETHER THE PROJECT IS NEW CONSTRUCTION, REMOVAL OF EXISTING WATERPROOFING, OR WATERPROOFING OVER EXISTING WATERPROOFING.]

˙

### New Construction

#### Poured Normal Weight Structural Concrete Deck:

The surface shall be equivalent to a smooth float finish and shall be free of dust, excess moisture, oil-based curing agents and loose debris.  Sharp ridges or other projections above the surface shall be removed before waterproofing.  Depressions and honeycombs shall be patched with SikaQuick® 1000 repair mortar.  Repair cracks in concrete up to 3/8 inch (9.5 mm) with Sikadur® Crack Fix epoxy or Sikadur® 35, Hi-Mod LV.  Cracks greater than 3/8 inch (9.5 mm) shall be repaired with SikaGrout® 212 non-shrink, cementitious grout.

### Removal of Existing Waterproofing

General Criteria

All existing overburden, waterproofing, base flashing, deteriorated wood blocking or deteriorated metal flashings shall be removed.  Remove only that amount of waterproofing and flashing that can be made weathertight with new materials during a one-day period or before the onset of inclement weather.

In areas to receive grid strips, all existing waterproofing must be removed down to clean concrete.  Waterproofing over existing coal tar pitch requires special consideration.  If coal tar residue remains on the deck and/or flashing substrate, refer to section 3.02.C.3. (Waterproofing Over Existing Waterproofing).

#### Poured Normal Weight Structural Concrete Deck:

The deck surface shall have a smooth and uniform finish and shall be free of dust, excess moisture, oil-based curing agents, loose debris, and loose, unbonded waterproofing materials.  Sharp ridges or other projections above the surface shall be removed before waterproofing.  Depressions and honeycombs shall be patched with SikaQuick® 1000 repair mortar.

### Waterproofing Over Existing Waterproofing

General Criteria

The Owner's Representative and Applicator shall determine the condition of the deck and existing waterproofing.  Deteriorated decking or wet or deteriorated materials are to be removed and replaced.  Remove all debris from the existing waterproofing.

#### Single-Ply

                - All loose single-ply waterproofing and flashings shall be removed.

#### Bitumen or Liquid Applied Waterproofing

                - Surface must be clean and dry.  All loose gravel and debris shall be removed by power brooming or vacuuming.  All blisters, ridges and irregularities shall be flattened.  Any accumulation of bitumen or other irregularities shall be scratched and removed so as to produce a smooth surface.

                - At locations where grid strips are to be installed, remove a minimum 14 inch (35.5 cm) wide strip of the existing waterproofing.  Remove all adhesive and/or waterproofing residue by grinding, sandblasting, grit blasting or other acceptable method to yield a clean concrete substrate.

                - At locations where control test drains are to be installed remove a 26 x 26 inch (66 x 66 cm) section of waterproofing.  Remove all adhesive and/or waterproofing residue by grinding, sandblasting, grit blasting or other acceptable method to yield a clean concrete substrate.

                - Vector Mapping Grid (VMG) for electronic leak detection testing must be installed between the existing waterproofing material and the Sarnafelt NWP-HD Leveling Layer.  See Section 3.05.

#### Coal Tar Pitch

#### Substrates to receive a Sika Sarnafil waterproofing system should have all coal tar pitch waterproofing and residue removed.  If a complete removal is not practical, substrates contaminated with coal tar pitch shall be treated as follows.

                - All coal tar pitch shall be completely removed at the perimeter, at grid strip locations, control test drain locations, and in all areas adjacent to flashings and penetrations by sand blasting, grit blasting or blast tracking.

                - Areas of coal tar pitch removal shall be a minimum of 18 inches (46 cm) wide.  The area shall be increased to 30 x 30 inches (76 x 76 cm) at control test drains.  If temperatures that will cause the coal tar pitch to creep or flow are expected, wider areas of removal are required.

                - Areas to receive G476 membrane shall be treated with a layer of Sarnavap-10.  Sealed the Sarnavap-10 to the clean concrete at the system perimeter and adjacent to all flashings, grid strips, and control test drains using a heavy bead of Sikaflex®-1a sealant.  Seal all overlaps, cuts and tears in the Sarnavap-10 with aluminum tape.

                - Vector Mapping Grid (VMG) for electronic leak detection testing must be installed between the Sarnavap-10 and the Sarnafelt NWP-HD Leveling Layer.  See Section 3.05.

###### CONTAINMENT GRID INSTALLATION

### Install 12 inch (30.5 cm) wide containment grids in accordance with layout shown on the project drawings and approved shop drawings.  The containment grids shall be installed at the base of all transitions, walls, curbs, penetrations, and below grade/low terminations.

### Install containment grid strips according to Sika Sarnafil’s most current installation instructions.  Installation of grid strips shall not proceed until a successful grid peel test is achieved. Test strips approximately 2 – 3 feet long shall be installed by the applicator to test the adhesion prior to the actual installation in representative areas. The applicator shall test the adhesion of the previous day’s grid installation by performing a peel test prior to starting the day’s grid installation. Refer to Sika Sarnafil’s most current quality assurance requirements for additional information.

### Install Sarnabar-SS fastened 12 inches (30 cm) on center with acceptable fasteners through the grid strip and into the structural deck, according to Sika Sarnafil detail drawings.  Hot-air weld Sarnacord-PVC onto the grid strip on the outside/penetration side of the Sarnabar-SS.  Weld a 4 inch (102 mm) wide membrane protection strip over bar ends and at bar intersections.

###### CONTROL TEST DRAIN INSTALLATION (If Specified)

### Install test drains according the Sika Sarnafil’s printed instructions.

### Control test drains shall be located according to the layout shown on the project drawings and approved shop drawings.

### The waterproofing system shall be installed continuously over the control test drains.

###### VECTOR MAPPING GRID AND CONNECTIONS INSTALLATION

[NOTE TO SPECIFIERS:  KEEP THIS SECTION IF VECTOR MAPPING GRID IS SPECIFIED IN SECTION 2.03]

    - Lay the Vector Mapping Grid (VMG) over the substrate. Overlap adjacent edges a minimum of 2 inches (50 mm).  Positive contact between adjacent sheets is required at both side and end laps.  Adjacent sheets may be taped together using duct or aluminum tape to prevent shifting.

    - Make sure the VMG contacts 1 – 2 inches of bare concrete while keeping it 1 – 2 inches away from the edge of the grid strip. Use a fastener and plate to secure VMG to the bare concrete in two places per grid containment area. Install the Leveling Layer over the Vector Mapping Grid as described below.

###### LEVELING AND SEPARATION LAYER INSTALLATION

### Install leveling layer over deck or Vector Mapping Grid (VMG). Spot adhere to deck to hold in place, if

### necessary.

### Trim edges of leveling layer even with the edge of the containment grid.

### Install only as much leveling layer as can be made weathertight at the end of each work day.

### Separation layer is installed above the membrane as additional protection as specified and according to the detail drawings lapping all edges a minimum of 4 inches (10.2 cm).

### The leveling/separation layer felt is to be cut with either scissors or utility blades.  The use of hot air welding equipment to cut the product is not allowed.

###### THERMOPLASTIC WATERPROOFING MEMBRANE INSTALLATION

### Comply with Sika Sarnafil’s most current installation instructions, specific recommendations, and approved shop drawings for this project.

### Workmen and all others that walk on waterproofing shall wear clean, soft-soled shoes so as not to damage materials. Heed all manufacturer’s cautions and warnings in regard to product use.  Membrane is slippery when wet or covered with frost, snow and ice.  Take proper precautions. Lay out work to minimize traffic over installed areas.

### Unroll and position the waterproofing membrane over the substrate.  Be sure to remove all shipping tape from the membrane.

###### HOT-AIR WELDING OF LAP AREAS

- General

#### All surfaces to be welded shall be clean and dry. No contaminants shall be present within lap areas.

#### Welding equipment shall be provided by or approved by Sika Sarnafil.  All mechanics intending to use the equipment shall be trained and qualified and shall have successfully completed a course of instruction provided by Sika Sarnafil’s representative prior to welding.

#### Adjacent sheets shall be welded in accordance with Sika Sarnafil’s instructions.  All side and end lap joints shall be hot air welded.  Lap area shall be a minimum of 3 inch (76.2 mm) wide when machine welding, and a minimum of 4 inch (10.2 cm) wide when hand welding.  Overlaps shall be with the flow of water where possible.

#### Hot-air weld waterproofing membrane and flashing membrane to grid strips as shown in Sika Sarnafil detail drawings.

- Machine Welding

#### Machine welded seams are achieved by the use of automatic welding equipment.  When using this equipment, Sika Sarnafil's instructions must be followed and local codes for electric supply, grounding and over current protection observed.  Dedicated circuit house power or a dedicated portable generator (30 A, 220 V, and recommended min. 7,500 Watts) is required.  No other equipment shall be operated off the generator.

- T-Joints (three-way overlaps)

The second layer (middle layer) of membrane of all T-Joints formed with membrane greater than 60-mils in thickness must be shaved down to create a smooth transition for the top layer of membrane prior to hot-air welding. A 4 inch (10.2 cm) round or square (with rounded corners) patch of max. 60 mil thick G476, G410, or G459 membrane must be hot-air welded over the center of the T-Joint intersection. The edges of the membrane forming the T-Joint  must be shaved to provide a smooth transition for the patch.

- Quality Control of Welded Seams

All completed welded seams shall be checked by the waterproofing Applicator after cooling for continuity using a rounded screwdriver or other suitable blunt object.  On-site evaluation of welded seams shall be made daily by the Applicator.  Cross-section samples shall be taken a minimum of two times a day (AM/PM) through completed seams and evaluated immediately. The samples must be dated and saved for evaluation by a Sika Sarnafil Technical Representative. Each test cut shall be patched by the Applicator.

###### MEMBRANE FLASHINGS

- All flashings shall be installed concurrently with the waterproofing membrane according to Sika Sarnafil approved details as the job progresses.  Flashings shall be adhered to compatible, dry, smooth, and solvent-resistant surfaces. All masonry joints shall be struck flush. Rough or incompatible surfaces may be covered with minimum 1/2 inch (13 mm) CDX plywood.

- When adhering to vertical surfaces greater than 30 inches (76.2 cm) in height, provide intermediate fastening of the flashing membrane according to Sika Sarnafil requirements.

- Complete the entire waterproofing assembly and flashing in a single working day; avoid exposure of any components to rain, snow, or dew.  If rain threatens during the day, or in an emergency, protect the unfinished exposed waterproofing and flashing components.

- All flashing membranes shall be mechanically fastened along the top edge according to approved Sika Sarnafil details.  Acceptable fasteners shall be used to secure flashings to substrate. Seal top of termination with an acceptable sealant.

- All flashings shall extend a minimum of 8 inches (20.3 cm) above the overburden unless previously accepted by the owner’s representative and/or design professional and Sika Sarnafil, in writing.

- All interior and exterior corners and miters shall be cut and hot-air welded into place.  Complete inside and outside corner flashing details with prefabricated corner patches (Sarnacorners).

- No bituminous elements shall be in contact with the waterproofing membrane, unless asphalt resistant membrane is used.  Flashing substrates contaminated with coal-tar shall be completely cleaned, or overlaid with minimum 1/2 inch (13 mm) thick CDX plywood or minimum 24 gauge stainless steel sheet metal.

###### SARNACLAD METAL FLASHINGS

- Complete all metal work in conjunction with waterproofing and flashings so that a watertight condition exists daily.

- Metal shall be installed to provide adequate resistance to bending and allow for normal thermal expansion and contraction.

- Metal joints shall be watertight.

- Metal flashings shall have a 4 inch (10.2 cm) minimum nailing flange and shall be fastened into solid wood blocking 4 inches (10.2 cm) on center staggered or into concrete with acceptable concrete anchors 6 inches (15.2 cm) on center staggered.  Fasteners shall penetrate the wood nailer a minimum of 1-1/4 inch (31.7 mm) or into concrete a minimum of 1 inch (25.4 mm).

- Adjacent sheets of PVC coated metal shall be spaced 1/4 inch (6.3 mm) apart.  The end joints of the metal shall be fastened 6 inches (15.2 cm) on center.  The joints shall be covered with 2 inch (50.8 mm) wide aluminum tape.  A 4 inch (10.2 cm) wide membrane flashing strip shall be hot air welded over the joint.

###### TEMPORARY CUT-OFF

- All flashings shall be installed concurrently with the membrane in order to maintain a watertight condition as the work progresses. Provide temporary cut-offs around exposed edges and at incomplete flashing areas from the new membrane to the structural deck or existing waterproofing.  Remove the cut-offs completely before proceeding with subsequent work.

- If inclement weather occurs while a temporary cut-off is in place, the Applicator shall provide the labor necessary to monitor the situation to maintain a watertight condition.

###### water testing of drains and Electronic leak detection testing

- The Applicator shall water test the drains for a minimum of 16 hours prior to the EFVM test. Plug the drain and flood with enough water to completely cover the clamping ring the day before the EFVM test. The Sika Sarnafil Technical Service Representative attending the EFVM test will inspect for leakage upon his arrival to the jobsite.

[NOTE TO SPECIFIERS:  IF VECTOR MAPPING GRID IS SPECIFIED IN SECTION 2.03, SELECT

B. 2. BELOW, OTHERWISE SELECT B. 1.]

### Electronic Leak Detection Testing

#### Follow Sika Sarnafil procedures for electronic leak detection testing over the completed waterproofing membrane to check for membrane water tightness prior to the installation of subsequent layers.

#### Perform EFVM electronic leak detection testing over the completed waterproofing membrane for testing of capillary defects and/or breaches in the membrane prior to the installation of subsequent layers.

- Should leaks be discovered, the Applicator shall locate leak source(s) and make repairs.  All patches/repairs shall be re-tested to assure watertightness.  All costs associated with the repairs shall be borne by the Applicator.

###### INSTALLATION OF DRAINAGE COMPOSITE

- Install drainage composite directly over the waterproofing membrane. Install drainage composite immediately after Sika Sarnafil’s inspection and acceptance of the waterproofing installation.

- Neatly trim drainage composite to fit closely around penetrations and at the base of all drains to ensure that water will flow freely from composite into drain openings.

- All cut edges of the drainage composite shall be covered in order to protect the waterproofing membrane from damage.

- Proceed with installation of insulation (if specified) or vegetative cover promptly.

###### INSULATION AND FILTER FABRIC INSTALLATION (If Specified)

- Insulation shall be laid in parallel courses with end joints staggered and tightly butted.

- Insulation shall be neatly cut to fit around penetrations and projections.

- Do not install more insulation than can be covered by overburden by the end of the day.

- Install filter fabric with proper overlaps according to manufacturer’s instructions.

- During installation in hot, sunny weather, the Applicator shall protect the insulation with a white covering to prevent excessive heat build-up and potential warping of the insulation boards.

###### PRECAST CONCRETE PAVER SYSTEM (If Specified)

- Prior to installation of the waterproofing system and pavers, inspect the deck for height and location of thresholds, stairs, and other major transition areas.

- Precast Pavers on Pedestals:

#### Install pavers according to the manufacturer’s published instructions.

#### Cut and fit pavers neatly at the base of walls and projections.

#### Shim or adjust pavers as required to provide a level surface with no more than 1/8 inch (3.2 mm) height differential.

#### Pavers will be power washed or cleaned to remove any laitance, dirt, or other unacceptable surface irregularities.

###### MONITORING THE VEGETATIVE COVER INSTALLATION

- The waterproofing Applicator shall monitor vegetative cover installation to assure no damage is done to the waterproofing membrane.

- Alert all parties concerned of any activities that might damage or adversely affect the long-term performance of the waterproofing.

###### DETAILS

Refer to system specific details at http://usa.sarnafil.sika.com.